## Main Material
Technical Section For NEW 132/33 KV SUBSTATION OF ABADAN OIL REFINERY (Main Substation)
No. | Description | QTY | Unit | Brand | Model | Origin | Unit Price | Total Price
1 | Fire Alarm Control Panel Vds Approval | 1 | Set | NSC | Solution F2 | Germany | - | -
2 | Addressable Smoke Detector with compatible base and Flashing LED Humidity Range: 0-95% Operating Voltage: 17-41Vdc Operating Temperature: -10°C to +50°C Protection degree: IP 42 Approval: LPCB & EN & VdS approved to classes A1 & C Material: White Polycarbonate Vds & LPCB Approval Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland, Plastic Backbox | 39 | Set | Hochiki | ALN-EN (WHT) + YBN/R3 (WHT) | UK | - | -
3 | Addressable Heat Detector with compatible base and LED Humidity Range: 0-95% Operating Voltage: 17-41Vdc Protection degree: IP 42 Material: White Polycarbonate Approval: LPCB & VdS approved to Classes A1, B & C Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland, Plastic Backbox | 1 | Set | Hochiki | ATJ-EN (WHT) + YBN/R3 (WHT) | UK | - | -
4.1 | Linear Heat Detector Rated voltage: 30Vac,42 Vdc Resistant: ~100Ω/km (29Ω/kft) per leg Alarm Temperature: 190°F (88°C) Operating Humidity range: sub-zero to 100 % condensing Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland, Clip | 150 | Meter | Thermocable | Proreact (88°C (190°F)) | UK | - | -
4.2 | Addressable Dual Input Module (For Linear Heat Detector) | 3 | Set | Hochiki | CHQ-DIM2(SCI) + CHQ-Back Box | UK | - | -
4.3 | Safe Area IP65 Junction Box (Zone Box for Linear Heat Detector) | 6 | Set | - | - | - | - | -
5 | Addressable Manual call point with short circuit isolator Indicator: Bi-colored status LED Operating Temperature Range -10 °C to + 50 °C IP Rating: IP24 rated Approvals: LPCB approved to EN54 Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland | 6 | Set | Hochiki | HCP-E(SCI) + SR Mounting + PS200 | UK | - | -
6 | Weatherproof Addressable Manual call point with short circuit isolator Indicator: Bi-colored status LED Operating Temperature Range -10 °C to + 50 °C IP Rating: IP67 rated Approvals: LPCB approved to EN54 Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland | 6 | Set | Hochiki | HCP-W(SCI) + PS-200 | UK | - | -
7 | Addressable Wall Sounder Beacon With Compatible Base Operating Voltage: 17 – 41 Vdc Operating Humidity: 95%RH - Non Condensing IP Rating: IP21 Approval: LPCB & VdS Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland | 5 | Set | Hochiki | CHQ-WSB2 + YBO-R/3(RED) | UK | - | -
8 | Addressable Weather Proof Wall Sounder Beacon With Compatible Base Operating Voltage: 17 – 41 Vdc Operating Humidity: 95%RH - Non Condensing IP Rating: IP65 Approval: LPCB & VdS Accessories: Stainless Steel Tag plate, 2 x Plastic Cable Gland | 5 | Set | Hochiki | CHQ-WSB2 + CHQ-WPK + YBO-R/3(RED) | UK | - | -
9 | Conventional Remote Indicator Accessories: Stainless Steel Tag plate, 1 x Plastic Cable Gland | 7 | Set | Hochiki | REM-E | - | - | -
10 | Conventional Explosion Proof Heat Detector Sensor: Semi-conductor Temperature Range: -20°C to +110°C Code of Protection: ATEX II 2G Ex d IIC T6 Protection Degree: IP65 (Probe IP67) Accessories: Stainless Steel Tag plate, 1 x Explosion Proof Cable Gland | 1 | Set | Oggioni | TMP2-JO-A1-R-1-A | UK | - | -
11 | Addressable Single Zone Module Accessories: Stainless Steel Tag plate, 3 x Plastic Cable Gland | 1 | Set | Hochiki | CHQ-SZM2(SCI) + CHQ-BACKBOX | UK | - | -
12 | Explosion Proof Manual Call Point Cable entrance holes: 2 Operating temperature: -20°C to +40°C Voltage: 24Vdc Approval: ATEX Classification and certification: Ex d IIC T6÷T4 Gb Material: Aluminum Color: RAL 3000 Protection degree: IP 66 Accessories: Stainless Steel Tag plate, 1 x Explosion Proof Cable Gland | 1 | Set | Coelbo | PB1-E1 | Italy | - | -
13 | Addressable Dual Input Module Accessories: Stainless Steel Tag plate, 4 x Plastic Cable Gland | 1 | Set | Hochiki | CHQ-DIM2(SCI) + CHQ-Back Box | UK | - | -
14 | H2 Gas Detector Range: 0-100% LEL Enclosure Material: ADC 12 aluminium alloy Approvals: ATEX and IECExEx II 2 G Ex db IIC T6 Gb Ex tb IIIC T80ᶜ Db II 2 G Ex db IIC T6 Gb Accessories: Stainless Steel Tag plate, 1 x Explosion Proof Cable Gland | 2 | Set | Crowcon | XGB-A1-01-A-ZA-R-FA | UK | - | -
15 | Addressable Plant Control Module (For Communication Between FACP & FECP) | 3 | Set | Hochiki | CHQ-PCM(SCI) + CHQ-Back Box | UK | - | -
16 | Address Programmer | 1 | Set | Hochiki | TCH-B200 | UK | - | -
Total Price | [7 empty] | 0
Special Tools (OPTIONAL)
1 | H2 Cylinder for Calibration, 50% LEL, with Fixed flow regulator and pressure gauge | 1 | Set | Local | - | Iran | - | -
2 | Smoke Tester with smoke aerosol and Telescopic Access Pole, Heat Tester | 1 | Set | Hochiki | Solo 330 + Solo A5 + Solo 461 + Solo 100 | UK | - | -
3 | Calibration adaptor + Weatherproof cap | 1 | Set | Crowcon | C03005 + C01442 | UK | - | -
Total Price | [7 empty] | 0
2-Years Spare Parts
No. | Description | QTY | Unit | Brand | Model | Origin | Unit Price | Total Price
1 | Addressable Smoke Detector with compatible base and Flashing LED | 3 | Set | Hochiki | ALN-EN (WHT) + YBN/R3 (WHT) | UK | - | -
2 | Addressable Multi Heat Detector with compatible base and LED | 1 | Set | Hochiki | ATJ-EN (WHT) + YBN/R3 (WHT) | UK | - | -
3 | Addressable Manual call point with short circuit isolator | 2 | Set | Hochiki | HCP-E(SCI) + SR Mounting + PS200 | UK | - | -
4 | Addressable Wall Sounder Beacon With Compatible Base | 2 | Set | Hochiki | CHQ-WSB2 + YBO-R/3(RED) | UK | - | -
5 | Addressable Plant Control Module | 1 | Set | Hochiki | CHQ-PCM(SCI) + CHQ-Back Box | UK | - | -
6 | H2 Gas Detector | 1 | Set | Crowcon | XGB-A1-01-A-ZA-R-FA | UK | - | -
7 | Linear Heat Detector | 50 | Meter | Thermocable | Proreact (88°C (190°F)) | UK | - | -
Total Price | [7 empty] | 0
Commissioning Spare Parts
No. | Description | QTY | Unit | Brand | Model | Origin | Unit Price | Total Price
1 | Addressable Smoke Detector with compatible base and Flashing LED | 1 | Set | Hochiki | ALN-EN (WHT) + YBN/R3 (WHT) | UK | - | -
2 | Addressable Multi Heat Detector with compatible base and LED | 1 | Set | Hochiki | ATJ-EN (WHT) + YBN/R3 (WHT) | UK | - | -
Total Price | [7 empty] | 0