## New 132Kv - Substation
Technical Section For NEW 132/33 KV SUBSTATION OF ABADAN OIL REFINERY (Main Substation)
No. | Description | QTY | Unit | Brand | Unit Price | Total Price
1 | IG-55 Cylinder Assembly: Completed with: 140 Lit 34 Cr Mo Cylinder Charged by IG-55 at 200 barg Supplier: Vitkovice-Czech -1 * High Flow Discharge Valve with Safety Burst Disc -1 * Pneumatic Actuator, -1 * Pressure gauge with Integrated Low-Pressure Switch -1 * Flexible Discharge Hose -1 * Flexible Actuation Hose with 2 connecting adaptor -1 * Manifold Discharge Check valve | 80 | Set | Vitkovice - Rotarex | - | -
2 | N2 Pilot Assembly: 3 Lit 34 Cr Mo Cylinder charged by N2 gas at 100 barg Container Sticker Supplier: Vitkovice – Czech Republic Completed with: 1 * High Flow Discharge Valve with Safety Burst Disc 1 * 24 V/DC Solenoid valve IP 65 1 * Manual Release Actuator + Safety Pin 1 * Pressure gauge with Integrated Low Pressure Switch 1 * Bracket Supplier: Local (Iran) | 5 | Set | Vitkovice - Rotarex | - | -
3 | Tube for Pilot cylinder and Fittings Supplier: Iran Market | 30 | Meter | Iran | - | -
4 | Bleed Valve for Pneumatic actuator | 5 | Set | Rotarex | - | -
5 | Pressure relief device for manifold | 2 | Set | Rotarex | - | -
6 | Pressure and flow detector / switch 2 Bar | 6 | Set | Rotarex | - | -
7 | Nozzle - IG | 40 | Set | Rotarex | - | -
8 | Directional Valve G3'', Pneumatic actuator | 2 | Set | Rotarex | - | -
9 | Directional Valve G2'', Pneumatic actuator | 4 | Set | Rotarex | - | -
10 | Self-standing Skid for IG-55 Cylinders, Hot Dip Galvanized Carbon Steel For 80 Cyl. Completed with all necessary accessories Supplier: Local | 1 | Set | Iran | - | -
11 | Discharge Manifold 3", Hot Dip Galvanized for 80 Cyl. Supplier: Local | 1 | Set | Iran | - | -
12 | Ristriction Orifice | 6 | Set | Rotarex | - | -
13 | Piping Material Including: Galvanized Support, pipe ASTM A53/A106 GR.B & Fitting between Cylinders till nozzles. Supplier: Local | 550 | Meter | Iran | - | -
14 | Lock-Out Valve + Position Switch Size: 3" Manufactured in carbon steel with spherical closing and Teflon seats. A manually operated valve in the discharge pipe between the nozzles and the agent supply that can be locked in the closed position to prevent flow of agent to the protected area. Supplier: Rotarex – Italy | 2 | Set | Rotarex | - | -
15 | Lock-Out Valve + Position Switch Size: 2" Manufactured in carbon steel with spherical closing and Teflon seats. A manually operated valve in the discharge pipe between the nozzles and the agent supply that can be locked in the closed position to prevent flow of agent to the protected area. Supplier: Rotarex – Italy | 4 | Set | Rotarex | - | -
16 | Status Panel including AMI switch, Hold off Unit and Manual Release Push Button Accessories: Name Plate, Plastic Gland | 6 | Set | Iran | - | -
17.1 | Extinguishing Control Panel Input Voltage: 230 VAC +10% - 15% Construction: 1.2mm mild sheet steel Color: RAL 7047 light grey Enclosure: IP30 With Auto/Manual Switch and Manual Release push button (with cover) EN12094-1, EN54-2 and EN54-4 Approved Complete with: 2 × 12 V Backup battery Supplier: Iran Market Accessories: Name Plate, Plastic Gland | 1 | Set | Kentec | - | -
17.2 | Extinguishing Control Panel Input Voltage: 230 VAC +10% - 15% Construction: 1.2mm mild sheet steel Color: RAL 7047 light grey Enclosure: IP30 With Auto/Manual Switch and Manual Release push button (with cover) EN12094-1, EN54-2 and EN54-4 Approved Complete with: 2 × 12 V Backup battery Supplier: Iran Market Accessories: Name Plate, Plastic Gland | 1 | Set | Kentec | - | -
18 | Weather Proof Entry Forbidden Warning Light Voltage: 24VDC Housing material: Self-extinguishing thermoplastic Protection degree: IP65 Installation Location: Wall Type Label: Entry Forbidden Lamp: High luminosity LED Intermittency frequency: Fixed light or 60/min With internal buzzer Accessories: Name Plate, Plastic Gland | 6 | Set | CSA | - | -
19 | Weather Proof Immediate Exit Warning Light Voltage: 24VDC Housing material: Self-extinguishing thermoplastic Protection degree: IP65 Installation Location: Wall Type Label: mmediate Exit Lamp: High luminosity LED Intermittency frequency: Fixed light or 60/min With internal buzzer Accessories: Name Plate, Plastic Gland | 6 | Set | CSA | - | -
20 | Fire Alarm Bell Accessories: Name Plate, Plastic Gland, Plastic Back Box | 5 | Set | Hochiki | - | -
21 | POWDER FIRE EXTINGUISHER (9 kg) -Agent weight:9KG -Name company :alborz nejat -Name brand:pishro -Type:Wheeled, dry chemical, External Design code:ISIRI -Fire class:BC/ABC -Test pressure:30 Bar -Test pressure worker:15 Bar -Color:red/Electorostatic | 10 | Set | Iran | - | -
22 | Wheeled DP Extinguisher (50 kg) -Agent weight:50KG -Name company :alborz nejat -Name brand:pishro -Type:Wheeled, dry chemical, External Design code:ISIRI -Fire class:BC/ABC -Test pressure:30 Bar -Test pressure worker:15 Bar -Empty weight:30 Kg -Full weight:80 Kg -Height:1040 mm -Diameter:300 mm -Color:red/Electorostatic | 5 | Set | Iran | - | -
23 | Portable CO2 Extinguisher 6 KG -Material : Steel -Extinguishant: Carbon Dioxide co2 Propellant Type: Stored -Pressure Capacity:6 Kg Paint colour: Signal red -Fire class:B+ Electrical -Operating Temperature:-20 to + 60 c Test pressure: 225 . 250 Bar Minimum -Discharge time:15 sec Discharge Range:4 m -Safe operating Distance:3 m / Operating Valve: Brass Hot Stamping -Discharge Nozzle: Hose & Horn -Height :71 cm / Diameter:140 mm -Full Weight:16 Kg / Empty Weight :11 Kg -Approval: ISIRI -With Cabinet Carbon Steel | 21 | Set | Iran | - | -
24 | Wheeled Co2 Extinguisher (30 kg) -Agent weight:30KG -Name company : alborz nejat Name brand: pishro -Design code: ISIRI -Fire class: BC/ABC -Test pressure:30 Bar -Color: red/Electorostatic | 3 | Set | Iran | - | -
Total Price | [5 empty] | 0
No. | Description | QTY | Unit | Brand | Unit Price | Total Price
Two Years Spare Parts
1 | Discharge flexible hose with check valve | 5 | _ | _ | - | -
2 | Actuation Hose | 5 | _ | _ | - | -
3 | Pneumatic Actuator | 5 | _ | _ | - | -
4 | Pressure Gauge with Integrated Low Pressure Switch | 5 | _ | _ | - | -
Total Price | [5 empty] | 0
Commissioning Spare Parts
1 | Discharge flexible hoses with check valve for IG55 system | 3 | _ | _ | - | -
2 | Actuation Hose for IG55 system | 3 | _ | _ | - | -
Total Price | [5 empty] | 0